# AHWR Digital Twin

Production rollout execution plan, ownership model, and rig-edge / central hardware requirements

Purpose: A practical handoff document for the teams responsible for OT/PLC access, rig hardware, networking and cybersecurity, edge deployment, central infrastructure, application configuration, testing, training, and ongoing support.

| Document field | Value |
| --- | --- |
| Scope | Production rollout to 50 rigs with one standardized indoor edge system per rig and an HA central CRMF |
| Deployment principle | Monitoring only; no command or control write-back to PLCs |
| Planning horizon | Wave-based production rollout; rig operating schedules and approved maintenance windows control duration |
| Prepared | 27 July 2026 |
| Status | Production rollout baseline — proving completed; apply per-rig commissioning and wave acceptance controls |

This plan is based on the repository’s proposal, deployment guide, Docker/Helm/Ansible assets, and current application status. Site drawings, ONGC standards, approved vendors, cybersecurity policy, and actual tag volumes remain controlling inputs.

# 1. Executive implementation decision

Proceed directly with production rollout in two controlled layers. Deploy the production HA central CRMF for 50 rigs, then install the standardized indoor edge package in approved waves. Each rig remains locally autonomous during WAN loss and uses authenticated outbound store-and-forward. The proven design is fixed; site-specific tag mapping, installation, commissioning, and acceptance remain mandatory for every rig.

Non-negotiable safety boundary: The solution receives and displays telemetry only. Do not create any PLC write route, control command, remote actuation, or central-to-rig operational path. ESD, lockout, BOP, accumulator, and related states are read-only alarms.

# 2. Delivery outcomes and scope boundaries

Rig-edge HMI with live, correctly scaled telemetry, local historian, alarms, workover activity, reports, maintenance, user roles, and honest stale/no-data indication.

Offline resilience: local HMI remains available during WAN loss; queued central batches replay oldest-first after restoration.

Central CRMF with rig registry, authenticated ingestion, fleet overview, per-rig drill-down, data-quality monitoring, cross-rig alarms, reports, governance, audit, and operations monitoring.

Repeatable installation pack: approved hardware BoQ, panel/network drawings, golden software image, tag workbook, test evidence, training records, rollback procedure, and support contacts.

Excluded from the production release:

ETP/WITSML central server, ML inference, Kafka derived-channel processor, and standalone MQTT-to-Kafka bridge where repository manifests are explicitly scaffolded or set to zero replicas.

Historical scrub-back replay UI, full ETP Avro encoding, direct SMS provider, and any unimplemented safety logic such as kick detection.

Any claim that missing BOP/ESD or other critical field tags are validated merely because synthetic demo data is visible.

# 3. Hardware requirements

## 3.1 Rig-edge hardware — one workover rig

| Item | Minimum / mandatory specification | Recommended production choice | Qty. |
| --- | --- | --- | --- |
| Industrial edge computer | Indoor industrial or enterprise-grade edge PC; 4 CPU cores; 16 GB RAM; 512 GB enterprise/industrial SSD; dual Ethernet; TPM 2.0; approved AC or 24 V DC supply | 4–8 cores, 16–32 GB RAM, 1 TB high-endurance SSD; vendor lifecycle ≥5 years | 1 |
| Operator HMI | 23.8–24 inch Full HD monitor for indoor control-room use | Commercial/industrial touch display if operator workflow requires touch; second display optional | 1 |
| Industrial switch | 8-port managed Ethernet switch; VLAN, RSTP and port security | SNMP/syslog, spare ports and approved redundant power where available | 1 |
| Firewall / VPN router | Approved firewall/router; VPN, NAT and ACL; separate OT and WAN interfaces | HA-capable model where the rig network design requires device redundancy | 1 |
| Protocol gateway | OPC UA / Modbus / S7 gateway when direct read-only PLC access is not approved | Dual-port isolated gateway with store diagnostics | As needed |
| Serial converter | Isolated RS-485/Ethernet converter for legacy Modbus RTU | Industrial temperature range and surge isolation | As needed |
| UPS | Online UPS; ≥30 minutes for edge PC, display, switch and router | Monitored UPS with replaceable battery and graceful-shutdown contact | 1 |
| Panel enclosure | Lockable ventilated indoor cabinet/rack; MCB, surge protection, earthing and cable management | Panel temperature and power-health monitoring; forced ventilation only if heat study requires it | 1 |
| Keyboard / pointing device | Standard business-grade keyboard and pointing device | Sealed type only where housekeeping or spill risk requires it | 1 |
| Time source | ONGC NTP | GPS/NTP appliance only where network time is unavailable | Optional |
| Cold standby | Required rollout resilience item | Pre-imaged spare edge PC or recoverable golden SSD | 1 per rollout group |

Sizing basis: Indoor installation; fewer than 500 tags per rig at 1-second sampling; 90 days local raw-data retention. This ceiling equals fewer than 43.2 million values/day and fewer than 3.89 billion values over 90 days per rig. Use a 1 TB high-endurance SSD as the rollout standard unless the accepted proving data supports a smaller device.

## 3.2 Central production workload — 50 rigs

| Component | Baseline | Notes |
| --- | --- | --- |
| Workload ceiling | 50 rigs × <500 tags × 1 Hz = <25,000 values/second | <2.16 billion values/day when every edge value is centralized |
| Recommended retention tier | 90 days central raw 1 Hz + 5 years of 1-minute aggregates | Keeps operational replay while controlling long-term volume |
| Availability target | RKE2 HA across three failure domains; central availability ≥99.5% | No single control-plane, worker, database or ingress failure stops service |
| Network | Redundant data-centre LAN; TLS ingress; VPN/private WAN; 1/10 GbE server links | Publish portal and ingest through controlled gateway; never expose the database |

## 3.3 Central production HA hardware baseline

Sizing basis: Fixed production ceiling of 50 rigs and fewer than 25,000 values/second. Storage assumes 90 days of raw 1 Hz telemetry at a conservative 8–20 compressed bytes/value, three database copies, WAL and operating headroom. Substitute the accepted measured compression figure if the completed proving record is more conservative.

| Tier | Recommended node specification | Qty. | Purpose / storage |
| --- | --- | --- | --- |
| RKE2 control plane | 8 vCPU, 32 GB RAM, 200 GB enterprise SSD, dual 10 GbE | 3 | etcd/control plane; spread across failure domains |
| General worker | 16 vCPU, 64 GB RAM, 500 GB OS/container SSD, dual 10 GbE | 3 | App, ingress, identity, MQTT and monitoring; ≥30% headroom |
| Data worker | 24 vCPU, 128 GB RAM, 1 TB local NVMe plus CSI-backed enterprise storage | 3 | Dedicated TimescaleDB/Kafka placement and storage bandwidth |
| TimescaleDB persistent storage | 5 TB data + 500 GB WAL per database instance | 3 sets | ≈16.5 TB allocated primary-site storage including three copies |
| Kafka storage (if enabled) | 500 GB enterprise SSD per broker | 3 | Replication factor 3; min in-sync replicas 2 |
| Backup / object storage | 20 TB usable protected object storage; expandable | 1 service | Database backups, WAL archive, reports and recovery headroom |
| DR site | Compute and storage capable of the same 50-rig database workload | 1 site | At least two DB replicas; size to approved RPO/RTO and retention |
| Load balancer / VIP | Redundant L4/L7 load balancer or approved managed equivalent | 2 or managed | RKE2 API and application ingress |

Production platform minimum service shape:

CRMF backend: start with 3 replicas and autoscale to 12; frontend: 3 replicas. Preserve at least 30% cluster headroom.

TimescaleDB: 3 instances; production override target per instance: 8 CPU / 32 GiB requested and up to 16 CPU / 64 GiB limited.

Kafka, when enabled: 3 brokers; target at least 2 CPU / 8 GiB and 500 GB enterprise storage per broker.

Keycloak: 2 instances plus a 2-instance PostgreSQL cluster; Timescale connection pooler: 2 instances.

EMQX, when MQTT is enabled: use three instances with discovery; do not use the single-instance repository default in production.

## 3.4 Fixed production sizing inputs and controls

| Input | Owner | Required decision |
| --- | --- | --- |
| Active rigs | Program PMO | 50 production rigs |
| Tags and edge retention | OT + data engineering | <500 tags/rig, 1 Hz, 90-day edge raw retention |
| Central ingest ceiling | Central platform | <25,000 values/s; <2.16 billion values/day |
| Central retention | Data owner / DGC | 90-day raw 1 Hz + 5-year 1-minute aggregate baseline |
| Report/object volume | Application owner | 20 TB protected object/backup tier with expansion path |
| Backup RPO/RTO and DR | Business continuity | Apply approved production RPO/RTO and recovery-test schedule |
| Portal performance | Operations | 50-rig dashboard SLA: normal filters load in <5 seconds |

# 4. Step-by-step implementation plan

Completed inputs: The production tag set has been identified and the edge-system configuration baseline has been finalized. The rollout must deploy that approved baseline; tag or configuration changes are handled only as controlled rig-specific exceptions.

## Step 0 — Release the production rollout baseline

Freeze the 50-rig wave schedule, approved hardware/software release, site owners, maintenance windows and change-control route.  Exit: Wave authorization, rig list, accountable owners and release version are signed.

## Step 1 — Confirm site readiness

Confirm the indoor cabinet/rack, power, UPS, earthing, LAN/WAN, fixed IPs, DNS/NTP, PLC route and installation access for each rig.  Exit: The site-readiness checklist and installation window are approved.

## Step 2 — Bring the production CMF foundation online

Deploy the Section 3 HA compute, storage, load balancer, RKE2, TLS, identity, backup/DR and monitoring baseline.  Exit: Cluster health, failover, backup/restore and security controls pass.

## Step 3 — Stage and test edge kits

Load the golden OS and signed application release, apply host hardening, verify UPS/runtime health and record each asset/version.  Exit: Each kit passes FAT and the spare/recovery image is usable.

## Step 4 — Pre-register rigs and credentials

Create the 50 permanent DEVICE_ID records, business metadata and unique per-rig tokens; transfer tokens through the approved secret channel.  Exit: Rig registry and credential-custody records are complete.

## Step 5 — Install the edge hardware

Mount the indoor cabinet/rack equipment, connect power/UPS, HMI, managed switch, firewall and approved PLC/gateway link; update as-built records.  Exit: Power, network, labels, earthing and physical installation checks pass.

## Step 6 — Deploy the approved edge baseline

Install the finalized configuration and set only rig-specific identity, token, PLC endpoint, network values and 90-day retention. Do not redesign the tag map during rollout.  Exit: All production containers are healthy and demo services are absent.

## Step 7 — Commission rig telemetry

Enable the approved tags and spot-check critical values, units, scaling, timestamp, 1 Hz history, alarms and stale/no-data behavior against the rig PLC/HMI.  Exit: The rig-specific commissioning sheet is signed; exceptions are disabled and recorded.

## Step 8 — Connect and synchronize with CMF

Verify outbound HTTPS authentication, telemetry counts, sequence acknowledgements and data quality; perform WAN loss, local-continuity and replay checks.  Exit: The rig is online, wrong credentials fail closed and the buffer drains after restoration.

## Step 9 — Complete SAT and security acceptance

Execute the Section 7 acceptance matrix for the installed rig and associated CMF functions, including role, exposure, report, backup and resilience checks.  Exit: No safety or critical defect remains open and all required signatories approve go-live.

## Step 10 — Train, hand over and go live

Train operators and administrators; issue L1/L2/L3 runbooks, contacts, backup instructions and incident/change procedures.  Exit: Training, operating certificate and support ownership are signed.

## Step 11 — Stabilize the wave and release the next

Run wave hypercare, review health, storage, incidents, data quality, adoption and open defects, then incorporate controlled lessons into the next deployment.  Exit: Wave KPIs are stable and governance authorizes the next wave.

# 5. Network, security and integration checklist

| Flow | Direction | Typical port | Rule / control |
| --- | --- | --- | --- |
| PLC to collector | Edge initiates to PLC/gateway | S7 TCP 102; Modbus TCP 502; OPC UA site-defined | Read-only; allowlisted edge IP; no route from central |
| Edge HMI | Operator workstation to edge frontend | TCP 8080 or approved HTTPS proxy | Bind only to approved rig LAN interface; authenticated |
| Edge to CRMF ingest | Outbound edge to central | HTTPS TCP 443 | VPN/private WAN, TLS, per-rig bearer token; gzip batches |
| DNS | Edge/central to approved resolver | UDP/TCP 53 | Approved resolvers only |
| NTP | Edge/central to approved time source | UDP 123 | Common authoritative time; alert on drift |
| AD/LDAP | Application to directory | LDAPS TCP 636 or StartTLS | Service account least privilege; certificate validation enabled |
| Registry / updates | Nodes to approved registry | HTTPS TCP 443 | Prefer internal Harbor and signed/scanned images |
| Central portal | Users to ingress | HTTPS TCP 443 | SSO/RBAC, WAF/rate limits, audit |
| Monitoring / logs | Platform to monitoring/SIEM | Site-defined | No secrets in logs; retention and alert routing approved |
| Database | Backend/internal only | PostgreSQL TCP 5432 | Never internet/WAN exposed; network policy and least-privilege role |

Cybersecurity completion checks:

OT and IT/WAN are separate zones; only explicit flows are allowed and documented.

No Docker socket is mounted into application containers; backend and historian are internal-only.

Production TLS validates the issuing CA; self-signed bypass settings are prohibited outside a controlled lab.

Real secrets are stored outside source control and rotated after any exposure; break-glass credentials are sealed and tested.

All nodes are patched to approved baselines; images are pinned, scanned, and promoted through controlled registry stages.

Login, configuration, alarm acknowledgement, user administration, report edits, device-token rotation, and privileged actions are auditable.

# 6. Configuration and data handoff checklist

| Artifact | Producer | Receiver | Acceptance rule |
| --- | --- | --- | --- |
| Master tag workbook | OT / instrumentation | Edge app + QA | Addresses, types, units, scaling and ranges signed |
| Alarm philosophy and setpoints | Operations / process safety | Application config | Priority, delay, deadband and response approved |
| Network/IP/port schedule | Network architect | Rig + central teams | ACLs implemented and tested from source to target |
| Certificate and secret custody | Cyber / platform | Named admins | Unique, approved channel, expiry/rotation recorded |
| Rig master and well metadata | Operations data owner | CRMF / edge app | Stable identifiers; no duplicate rig IDs |
| Golden image and software bill | Platform team | Support / vendor | Hash/version recorded; restore test passed |
| As-built drawings and photos | Installation vendor | Asset owner | Redlines closed and approved |
| Test pack and defect register | QA | All stakeholders | Evidence traceable to acceptance criteria |
| Runbooks and escalation matrix | Support manager | L1/L2/L3 teams | On-call contacts and SLAs acknowledged |

# 7. Minimum acceptance matrix

| Area | Mandatory test | Pass criterion | Sign-off |
| --- | --- | --- | --- |
| Data acquisition | Compare agreed critical tags with PLC/HMI | Correct value, unit, scaling and timestamp; missing tags explicit | OT + operations |
| Live dashboard | Observe real operation and stale source | ≈1 s local updates; stale/no-data shown honestly | Operations |
| Alarms | Trigger representative priorities | State, delay, deadband, ack and history correct | Operations + safety |
| Reports | Generate daily and connection records | Complete, correct date/well/rig scope; export usable | Operations |
| Security | Role and negative-access tests | Admin/operator/viewer boundaries enforced server-side | Cyber + QA |
| Offline edge | Disconnect WAN | Local HMI/historian remain operational | Rig + QA |
| Central sync | Outage, buffer, restore and replay | Backlog drains; central reflects full allowed interval | Network + QA |
| Identity | AD/LDAP/SSO and break-glass | Mapped roles correct; emergency local access controlled | IAM + app owner |
| Reliability | Continuous production soak | Meets agreed uptime; no uncontrolled disk growth | Support owner |
| Backup / DR | Restore database/configuration | Recovery meets approved RPO/RTO | Infrastructure + business continuity |
| Performance | Full 50-rig / <25,000 values/s production profile | Portal <5 s for normal filters; ingest and latency meet approved SLA | Performance QA |
| Training | Operator and admin assessment | Attendance and competency sign-off complete | Operations owner |

# 8. Operations and support model

| Level | Typical responsibility | Escalate when |
| --- | --- | --- |
| L1 — Rig / NOC | Availability check, user assistance, cable/power/network checks, standard restart/runbook, incident ticket | Data stale after basic checks; repeated alarm/report issue |
| L2 — OT / platform | PLC/gateway diagnostics, tag/scaling, container/storage/network health, token/certificate, backup | Code defect, schema defect, security issue, unresolved data loss |
| L3 — Product engineering | Backend/frontend defects, database migration, performance, release and hotfix | Architecture/vendor/enterprise dependency decision |
| L4 — Vendor / enterprise | Hardware warranty, PLC vendor, WAN carrier, AD/PKI, storage and platform operator | Contractual or shared-service fault |

Daily: edge/central health, freshness, buffer, disk, backup job and critical security alerts.

Weekly: data-quality score, missing tags, alarm recurrence, NPT classification, open defects and capacity trend.

Monthly: patch/release review, restore sample, user/role review, token/certificate expiry, asset/UPS health and value metrics.

Quarterly: DR exercise or tabletop, vulnerability review, retention/capacity forecast, architecture and rollout standard review.

# 9. Wave release and completion gate

A production wave may be released or closed only when all of the following are true:

The previous wave or central foundation acceptance is signed and no safety/critical defect remains open.

Real critical tags—not demo signals—have been validated with scaling evidence.

Edge survives WAN outage and central replays the buffered interval correctly.

Hardware kit, panel drawing, network design, golden image, and installation method are repeatable.

The central platform remains within the fixed 50-rig CPU, memory, storage, ingest, backup and DR operating envelope.

Cybersecurity approval, secret custody, audit, patching, and incident response are operational.

Operators and support teams have signed training and handover.

DGC/program governance has approved the wave, funding, rig list and named accountable owners.

# 10. Known implementation cautions from the current repository

| Caution | Required action before acceptance |
| --- | --- |
| Repository central PVC and pod defaults are undersized for the fixed 50-rig workload | Override with Section 3 production values before deployment; monitor measured bytes/value and ingest headroom |
| Several central services are scaffolds or disabled | Keep out of scope or fund/build/test separately; do not count them as delivered |
| Historian history is not yet full min/max-envelope replay | Agree reporting/replay limitations and prioritize if operationally required |
| Some safety signals may differ by rig PLC implementation | Commission every critical signal at the target rig and record disabled/unavailable tags |
| Audit coverage at edge may not include every privileged operational action | Perform audit-gap review and close actions required by ONGC policy |
| Current central raw retention defaults to five years | Change to the approved 90-day raw tier plus 5-year aggregates, or fund a much larger archive tier |

# 11. Reference basis

Repository README.md — rig-edge architecture, local deployment, PLC integration and security model.

central/README.md — CRMF architecture, portal modules and edge ingestion contract.

docs/DEPLOYMENT.md — edge/central deployment, device registration, networking, signal-flow verification and operations.

ONGC-DGC-AHWR-Digital-Twin-Proposal.md — roadmap, rig hardware, central requirements, cybersecurity and acceptance criteria.

central/deploy/README.md and deployment manifests — RKE2 platform topology, service replicas, requests, limits, storage and DR design.

PENDING-WORKS.md — current implementation gaps and delivery cautions.

# 12. Central platform terminology

This glossary explains the infrastructure terms used in the hardware and installation sections. It is intended for operational, procurement and management counterparts as well as platform engineers.

| Term | Plain-language meaning | Why it matters |
| --- | --- | --- |
| RKE2 | A security-focused Kubernetes distribution used to run and manage CMF services across multiple servers. | Restarts failed workloads, distributes applications and supports controlled upgrades. |
| Kubernetes | A platform that schedules and manages containerized applications. | Provides a common operating layer across the central servers. |
| Control plane | The Kubernetes servers that hold cluster state and make scheduling decisions. | Three nodes provide quorum and tolerate one control-plane failure. |
| Worker node | A server that runs application or data workloads. | General workers run portal services; data workers run database and messaging workloads. |
| HA | High Availability: multiple instances and failure paths prevent a single fault from stopping service. | Required for the central 50-rig service. |
| PostgreSQL | The relational database engine used for operational and master data. | Stores rigs, users, alarms, governance, audit and related records. |
| TimescaleDB | A PostgreSQL extension optimized for timestamped telemetry. | Stores and queries rig measurements efficiently. |
| WAL | Write-Ahead Log: every database change is written to a recovery log before the main data files. | Enables crash recovery, standby replication and point-in-time restore. |
| PVC | Persistent Volume Claim: a Kubernetes request for durable storage. | Keeps database data after a container restarts or moves to another node. |
| CSI | Container Storage Interface: the standard link between Kubernetes and SAN, Ceph, Longhorn or another storage platform. | Allows approved enterprise storage to supply persistent volumes. |
| Ingress | The controlled HTTPS entry point that routes portal, API, WebSocket and ingest requests. | Gives consumers and edges one governed CMF address. |
| Load balancer / VIP | A redundant front door and stable virtual IP that sends traffic to healthy services. | Maintains access when one ingress or server fails. |
| TLS / HTTPS | Encryption and server authentication for network traffic. | Protects office and rig-to-CMF communications. |
| SSO | Single Sign-On using the corporate identity provider. | Lets office users use their approved enterprise account. |
| RBAC | Role-Based Access Control. | Limits functions and data according to viewer, operator or administrator role. |
| Kafka | A distributed event-streaming platform. | Optional distribution path for high-volume enterprise consumers; not required for the core portal/API. |
| MQTT / EMQX | MQTT is a lightweight telemetry protocol; EMQX is an MQTT broker. | Optional alternative integration route when enabled and approved. |
| Object storage | S3-compatible storage for backups, reports and exported files. | Keeps large objects and recovery data outside the live database. |
| DR | Disaster Recovery at an independent site. | Restores or assumes service if the primary data centre is unavailable. |
| RPO | Recovery Point Objective: maximum acceptable data loss measured in time. | Determines backup and replication frequency. |
| RTO | Recovery Time Objective: maximum acceptable restoration time. | Determines recovery automation and standby capacity. |
| Aggregate | A lower-resolution summary such as one-minute average, minimum and maximum. | Supports long retention without storing every 1 Hz value indefinitely. |

# 13. Access for consumers at other office locations

Access principle: Office consumers access one internal CMF address through the ONGC corporate WAN or approved VPN. They must not connect to rig PLCs, rig-edge databases, the primary CMF database, Kubernetes management ports or backup administration interfaces.

Recommended traffic path: Rig edge systems send outbound HTTPS telemetry to CMF. Office users and approved applications connect to https://crmf.ongc.local over HTTPS/WSS port 443. The CMF ingress authenticates and routes requests to the portal, REST API or live WebSocket service.

| Consumer | Access method | Permitted use | Mandatory control |
| --- | --- | --- | --- |
| Operations and management | CMF browser portal | Fleet overview, rig drill-down, alarms, data quality, workover, reports and governance | AD/OIDC SSO and RBAC |
| Live office display | Portal + secure WebSocket | Initial state from REST API; live changes through WSS | HTTPS/WSS 443 only; viewer account |
| Internal application | Versioned CMF REST API | Latest values, history, alarms, health, wells and reports | Dedicated read-only service identity, rate limit and audit |
| BI / reporting | Reporting replica, curated views or scheduled export | Power BI/Tableau and departmental reports | No queries against the primary ingest database |
| Data science / data lake | Controlled batch export to object storage | One-minute aggregates and approved raw intervals | Partition by rig/date; catalogue, retention and bulk-download audit |
| Enterprise real-time integration | Kafka topics after separate production acceptance | Multiple authorized streaming consumers | Per-consumer credentials and topic ACLs; optional work package |
| Platform administration | Separate privileged administration network | Kubernetes, database and recovery operations | MFA, named accounts, jump host and full audit |

## 13.1 Office network onboarding procedure

- Confirm corporate connectivity: Verify that the office is on the approved ONGC WAN/MPLS/SD-WAN or VPN and can route to the CMF application zone.

- Publish internal DNS: Resolve crmf.ongc.local to the redundant CMF load-balancer VIP. Do not publish the address to the public internet.

- Open the minimum firewall flow: Allow office consumer networks to the CMF VIP on HTTPS/WSS TCP 443. Do not open PostgreSQL 5432, Kubernetes, Kafka administration, MQTT administration or rig subnets.

- Validate certificate trust: Ensure office devices trust the ONGC CA that issued the CMF TLS certificate.

- Create identity groups: Map corporate directory groups to CMF viewer, operator and administrator roles. Use viewer as the normal office-consumer role.

- Onboard applications separately: Issue a dedicated read-only service identity for each system integration; define API scope, rate limit, owner, expiry and audit requirements.

- Test and record access: Confirm login, authorized screens/API functions, denied functions, session timeout and audit logging from the target office.

## 13.2 Consumer security rules

No office consumer is given a rig IP address or direct route to a rig edge or PLC network.

No BI tool or ordinary application connects to the primary TimescaleDB service.

Human users use SSO; shared user accounts are prohibited.

System integrations use service identities with read-only scopes and documented owners.

Bulk exports follow data-classification, retention and audit policy.

All access is encrypted, logged and reviewed periodically.

# 14. Production edge installation procedure

Installation basis: Indoor edge system, fewer than 500 enabled tags, 1 Hz acquisition and 90-day local retention. Use the signed production release and a permanent unique DEVICE_ID. Never reuse a rig identity, production token or demo credential.

## 14.1 Prerequisites

Installed indoor edge PC, monitor, managed switch, firewall/router and UPS meeting Section 3.

Approved Linux LTS image, fixed IP addresses, DNS, NTP and host-hardening baseline.

Read-only PLC/gateway route and the signed rig-specific tag workbook.

Outbound HTTPS route to https://crmf.ongc.local and a generated per-rig device token.

Approved offline software bundle or access to the internal signed container registry.

Named edge administrator, operations representative and commissioning window.

## 14.2 Install the software

- Prepare the host: Apply the approved OS patches, hostname, fixed addressing, NTP, endpoint controls, disk monitoring and host firewall. Confirm the system clock before collecting data.

- Install the container runtime: Install approved Docker Engine and Docker Compose packages from the ONGC repository or offline bundle. Add only named platform administrators to the Docker administration group.

- Install the release files: Create /opt/ahwr-edge, extract the signed release bundle there, verify its checksum and record the application version.

sudo mkdir -p /opt/ahwr-edge
cd /opt/ahwr-edge
# Extract the approved release bundle here and verify its recorded checksum.
cp .env.example .env

- Create production configuration: Edit /opt/ahwr-edge/.env with secrets supplied through the approved secret channel. Restrict file permissions to the designated service administrator.

DEVICE_ID=AHWR-XX
DEVICE_TOKEN=<unique-token-issued-by-CMF>
CENTRAL_URL=https://crmf.ongc.local
SYNC_ENABLED=true
SYNC_BATCH_SECONDS=10
SYNC_BUFFER_DAYS=15
DATA_SOURCE=plc
INFLUX_RETENTION=90d
INFLUX_PASSWORD=<secret>
INFLUX_TOKEN=<secret>
JWT_SECRET=<secret>
ADMIN_PASSWORD=<secret>
FRONTEND_BIND=<approved-rig-LAN-IP>
FRONTEND_PORT=8080
AUTH_MODE=both
LDAP_URL=ldaps://<approved-directory>:636

- Validate configuration: Review the fully resolved Compose configuration before starting. Confirm that no database or backend port is published to an unapproved interface.

cd /opt/ahwr-edge
docker compose config

- Start the production stack: Use the approved production release path. The current repository builds locally; a registry-based deployment should use the approved prebuilt-image override.

cd /opt/ahwr-edge
docker compose up -d --build
docker compose ps

- Configure the PLC mapping: Open the edge HMI, sign in as an administrator, configure the approved S7/Modbus/OPC UA source and apply only the signed rig-specific tags. Confirm that every connection is read-only.

- Configure application masters: Configure users/roles, alarm setpoints, wells, activities, report headers, maintenance items and the approved dashboard layout.

- Commission local operation: Compare live values, engineering units, timestamps and stale/no-data behavior with the PLC/HMI. Confirm alarms, reports, 1 Hz history and the 90-day retention setting.

- Commission CMF synchronization: Confirm the rig is online in CMF, sequence acknowledgements increase and the edge buffer drains. Disconnect WAN, verify local continuity and buffer growth, restore WAN and confirm replay.

- Capture the installation record: Save the as-built drawing, host and application versions, device identity, tag-map version, encrypted configuration backup, health evidence, SAT record and support handover.

## 14.3 Edge verification checklist

| Check | Pass condition |
| --- | --- |
| Containers | All required services are running and healthy; demo-profile services are absent. |
| Local HMI | Authorized workstation reaches the HMI; backend and InfluxDB are not directly exposed. |
| Historian | 1 Hz data is present and retention is 90 days. |
| PLC interface | Enabled tags match the signed workbook; source is read-only. |
| Time | PLC/gateway, edge and CMF timestamps are synchronized. |
| Security | Production secrets, LDAPS/TLS, roles and host firewall are active. |
| Offline resilience | HMI continues during WAN loss; buffered batches replay after restoration. |
| Backup | Configuration and persistent application state can be restored to the golden spare. |

# 15. Production CMF installation procedure

Deployment basis: Use the HA RKE2, Helm and Ansible production path for 50 rigs. Do not use the single-host Docker Compose topology. Override the repository’s development-sized pod and PVC defaults with the Section 3 production values before deployment.

## 15.1 Infrastructure prerequisites

Three RKE2 control-plane nodes, three general workers and three data workers with fixed addresses and redundant 10 GbE connectivity.

Redundant load balancer/VIP, internal DNS name crmf.ongc.local and ONGC-issued TLS certificate/issuer.

Approved CSI storage classes providing three 5 TB database volumes, three 500 GB WAL volumes and the required Kafka volumes if enabled.

At least 20 TB protected object/backup storage and an approved independent DR target.

Internal Harbor registry, signed/scanned backend and frontend images, and node access to required system images.

Vault/External-Secrets integration for database, JWT, ingest, administrator, backup and identity secrets.

Connectivity to NTP, DNS, AD/OIDC, monitoring/SIEM, backup storage and corporate office networks.

## 15.2 Build the RKE2 platform

- Prepare deployment configuration: Copy the example Ansible inventory and variables into site-controlled files. Populate the real control-plane VIP, node groups, hostnames, storage classes, registry, TLS issuer and non-secret environment values.

cd central/deploy/ansible
cp inventory.example.ini inventory.ini
cp group_vars/all.example.yml group_vars/all.yml
# Edit the site files through approved configuration control.

- Keep secrets out of source control: Use Ansible Vault only where required during bootstrap and use Vault plus External-Secrets for runtime credentials. Do not place production passwords in committed YAML files.

- Apply production capacity overrides: Before installing data services, set TimescaleDB to three instances with 5 TB data and 500 GB WAL per instance and production resource targets of 8 CPU/32 GiB requested, up to 16 CPU/64 GiB limited. Apply the approved Kafka, object-storage and DR values.

- Bootstrap RKE2 and operators: Run the controlled Ansible site playbook from the administration workstation. This installs RKE2, the selected operators and the platform components defined by the repository.

cd central/deploy/ansible
ansible-playbook -i inventory.ini site.yml

- Confirm cluster readiness: Verify that all control-plane and worker nodes are Ready, time is synchronized, the storage classes are available and the default-deny network baseline is active.

kubectl get nodes -o wide
kubectl get storageclass
kubectl get namespaces

## 15.3 Deploy data and application services

- Provision database secrets and backup access: Materialize the database owner, least-privilege application login, superuser and backup credentials through External-Secrets/Vault. Ensure the backend uses the crmf_app login rather than the schema owner.

- Deploy TimescaleDB and platform services: Apply the approved CloudNativePG/TimescaleDB, backup, pooler, identity, object-storage, observability and optional messaging resources. Keep scaffolded or zero-replica components disabled.

- Build and promote application images: Use the approved CI pipeline to build, scan, sign and push backend/frontend images to Harbor. Pin the production release tag or immutable digest in the Helm values.

- Deploy the CMF application: Install or upgrade the production Helm release with three backend replicas, three frontend replicas, HPA, PDB, NetworkPolicy, ServiceMonitor, ingress and TLS enabled.

helm upgrade --install crmf central/deploy/helm/crmf \
  -n crmf -f central/deploy/helm/crmf/values-prod.yaml \
  --create-namespace

- Verify Kubernetes rollout: Confirm pods, persistent volumes, services and ingress are healthy. Verify the backend and frontend deployments complete their rollouts.

kubectl -n crmf get pods,pvc,svc,ingress
kubectl -n crmf rollout status deployment/crmf-backend
kubectl -n crmf rollout status deployment/crmf-frontend

- Verify internal health: Use a controlled port-forward or approved administration path to check the backend health endpoint without publishing it externally.

kubectl -n crmf port-forward svc/crmf-backend 6000:6000
# From a second terminal:
curl -fsS http://127.0.0.1:6000/healthz

## 15.4 Configure CMF and onboard rigs

- Configure identity: Connect AD/LDAP or OIDC, map viewer/operator/administrator groups and retain a sealed break-glass administrator.

- Configure production settings: Set the 90-day raw retention tier, five-year one-minute aggregates, offline threshold, notifications, audit, dashboards, metrics and alerts.

- Create the rig registry: Create all 50 stable rig identities and business metadata. Never reuse a simulator or retired DEVICE_ID.

- Issue per-rig credentials: Generate one device token for each rig and transfer it through the approved secret channel. Rotate immediately if custody is uncertain.

- Onboard one wave at a time: Verify telemetry counts, distinct metrics, timestamps, sequence acknowledgements, data-quality score, alarms and rig online state.

- Enable office consumers: Publish internal DNS, permit HTTPS/WSS 443 from approved office networks, enable SSO groups and test portal/API access according to Section 13.

## 15.5 CMF production acceptance

| Area | Production pass condition |
| --- | --- |
| HA | Loss of one control-plane, general worker, data worker or ingress instance does not stop the service. |
| Database | Primary and replicas are healthy; compression, retention, continuous aggregates and connection pooler are active. |
| Capacity | 50-rig / <25,000 values-per-second profile remains inside approved CPU, memory, storage and latency thresholds. |
| Backup / DR | Base backup, WAL archive, restore and DR promotion meet the approved RPO/RTO. |
| Security | TLS, SSO/RBAC, per-rig tokens, least-privilege DB role, NetworkPolicy, secrets and audit pass. |
| Office access | Authorized offices reach portal/API over 443; database, Kubernetes and rig networks remain inaccessible. |
| Operations | Dashboards, alerts, logs, capacity thresholds, runbooks and L1/L2/L3 escalation are active. |

Change control: Revise this report only through approved production change control. Record the version, approver, effective date, affected rigs/services, rollback method and change summary.